## Sheet1
Read Register from HORNER RCC 1410
Name | MODBUS ID | MODBUS COMAND SUPPORTED | Bit | Type | Data Type | OFFSET | R/W | Comments | PORT:502 SLAVE ID:1 | IP :
STATUS_D1 | 10001 | Read Input Status (2) | 1-OPEN 0-CLOSE | DI | BOOL | 0 | R | CLOSE/OPEN DC SWITCH FEEDBACK D1 | POLL:250 mSec
STATUS_D2 | 10002 | Read Input Status (2) | 1-OPEN 0-CLOSE | DI | BOOL | 1 | R | CLOSE/OPEN DC SWITCH FEEDBACK D2 | REACQUIRE TIME :1000 mSec
STATUS_D3 | 10003 | Read Input Status (2) | 1-OPEN 0-CLOSE | DI | BOOL | 2 | R | CLOSE/OPEN DC SWITCH FEEDBACK D3 | TIMEOUT: 1000 mSec
STATUS_D4 | 10004 | Read Input Status (2) | 1-OPEN 0-CLOSE | DI | BOOL | 3 | R | CLOSE/OPEN DC SWITCH FEEDBACK D4 | RETRIES:1/2
STATUS_D5 | 10005 | Read Input Status (2) | 1-OPEN 0-CLOSE | DI | BOOL | 4 | R | CLOSE/OPEN DC SWITCH FEEDBACK D5
STATUS_D6 | 10006 | Read Input Status (2) | 1-OPEN 0-CLOSE | DI | BOOL | 5 | R | CLOSE/OPEN DC SWITCH FEEDBACK D6
M_D1 | 1 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 6 | R | CHARGE SPRING D1
M_D2 | 2 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 7 | R | CHARGE SPRING D2
M_D3 | 3 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 8 | R | CHARGE SPRING D3
M_D4 | 4 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 9 | R | CHARGE SPRING D4
M_D5 | 5 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 10 | R | CHARGE SPRING D5
M_D6 | 6 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 11 | R | CHARGE SPRING D6
O_D1 | 7 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 12 | R | CLOSE COMMAND D1
O_D2 | 8 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 13 | R | CLOSE COMMAND D2
O_D3 | 9 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 14 | R | CLOSE COMMAND D3
O_D4 | 10 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 15 | R | CLOSE COMMAND D4
O_D5 | 11 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 16 | R | CLOSE COMMAND D5
O_D6 | 12 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 17 | R | CLOSE COMMAND D6
OF_D1 | 13 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 18 | R | OPEN COMMAND D1
OF_D2 | 14 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 19 | R | OPEN COMMAND D2
OF_D3 | 15 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 20 | R | OPEN COMMAND D3
OF_D4 | 16 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 21 | R | OPEN COMMAND D4
OF_D5 | 17 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 22 | R | OPEN COMMAND D5
OF_D6 | 18 | Read Coil Status (1) | 1-CLOSE 0-OPEN | Coil | BOOL | 23 | R | OPEN COMMAND D6
MAN_MOT_ON1 | 6001 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 0 | R/W | PUSH BUTON FOR CLOSE DC SWITCH D1
ON_D1 | 6002 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 1 | R/W | NOT USED
OFF_D1 | 6003 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 2 | R/W | PUSH BUTON FOR OPENING DC SWITCH D1
MAN_MOT_ON2 | 6004 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 3 | R/W | PUSH BUTON FOR CLOSE DC SWITCH D2
ON_D2 | 6005 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 4 | R/W | NOT USED
OFF_D2 | 6006 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 5 | R/W | PUSH BUTON FOR OPENING DC SWITCH D2
MAN_MOT_ON3 | 6007 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 6 | R/W | PUSH BUTON FOR CLOSE DC SWITCH D3
ON_D3 | 6008 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 7 | R/W | NOT USED
OFF_D3 | 6009 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 8 | R/W | PUSH BUTON FOR OPENING DC SWITCH D3
MAN_MOT_ON4 | 6010 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 9 | R/W | PUSH BUTON FOR CLOSE DC SWITCH D4
ON_D4 | 6011 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 10 | R/W | NOT USED
OFF_D4 | 6012 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 11 | R/W | PUSH BUTON FOR OPENING DC SWITCH D4
MAN_MOT_ON5 | 6013 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 12 | R/W | PUSH BUTON FOR CLOSE DC SWITCH D5
ON_D5 | 6014 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 13 | R/W | NOT USED
OFF_D5 | 6015 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 14 | R/W | PUSH BUTON FOR OPENING DC SWITCH D5
MAN_MOT_ON5 | 6016 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 15 | R/W | PUSH BUTON FOR CLOSE DC SWITCH D6
ON_D6 | 6017 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 16 | R/W | NOT USED
OFF_D6 | 6018 | Read Coil Status (1) | 1-CLOSE 0-OPEN | CONTACT NO | BOOL | 17 | R/W | PUSH BUTON FOR OPENING DC SWITCH D6
SPAM_ON_COND_D1 | 6050 | Read Coil Status (1) | 1-OPEN 0-CLOSE | CONTACT NC | BOOL | 49 | R | FEEDBACK STOP CONDITION D1
SPAM_ON_COND_D2 | 6051 | Read Coil Status (1) | 1-OPEN 0-CLOSE | CONTACT NC | BOOL | 49 | R | FEEDBACK STOP CONDITION D2
SPAM_ON_COND_D3 | 6052 | Read Coil Status (1) | 1-OPEN 0-CLOSE | CONTACT NC | BOOL | 49 | R | FEEDBACK STOP CONDITION D3
SPAM_ON_COND_D4 | 6053 | Read Coil Status (1) | 1-OPEN 0-CLOSE | CONTACT NC | BOOL | 49 | R | FEEDBACK STOP CONDITION D4
SPAM_ON_COND_D5 | 6054 | Read Coil Status (1) | 1-OPEN 0-CLOSE | CONTACT NC | BOOL | 49 | R | FEEDBACK STOP CONDITION D5
SPAM_ON_COND_D6 | 6055 | Read Coil Status (1) | 1-OPEN 0-CLOSE | CONTACT NC | BOOL | 49 | R | FEEDBACK STOP CONDITION D6
TIMER_MOT_D1 | 41513 | Read Holding register (3) |  | HOLDING REGISTER | INT 16 BIT | 0 | R | PRESET 3 S TON FOR ENERGYZING THE SPRING D1
TIMER_MOT_D2 | 41515 | Read Holding register (3) |  | HOLDING REGISTER | INT 16 BIT | 2 | R | PRESET 3 S TON FOR ENERGYZING THE SPRING D2
TIMER_MOT_D3 | 41517 | Read Holding register (3) |  | HOLDING REGISTER | INT 16 BIT | 4 | R | PRESET 3 S TON FOR ENERGYZING THE SPRING D3
TIMER_MOT_D4 | 41519 | Read Holding register (3) |  | HOLDING REGISTER | INT 16 BIT | 6 | R | PRESET 3 S TON FOR ENERGYZING THE SPRING D4
TIMER_MOT_D5 | 41521 | Read Holding register (3) |  | HOLDING REGISTER | INT 16 BIT | 8 | R | PRESET 3 S TON FOR ENERGYZING THE SPRING D5
TIMER_MOT_D6 | 41523 | Read Holding register (3) |  | HOLDING REGISTER | INT 16 BIT | 10 | R | PRESET 3 S TON FOR ENERGYZING THE SPRING D6
TIMER_ON_D1 | 41525 | Read Holding register (3) |  | HOLDING REGISTER | INT 16 BIT | 12 | R | PRESET 6 S TON FOR GIVING CLOSE COMAND D1
TIMER_ON_D2 | 41527 | Read Holding register (3) |  | HOLDING REGISTER | INT 16 BIT | 14 | R | PRESET 6 S TON FOR GIVING CLOSE COMAND D2
TIMER_ON_D3 | 41529 | Read Holding register (3) |  | HOLDING REGISTER | INT 16 BIT | 16 | R | PRESET 6 S TON FOR GIVING CLOSE COMAND D3
TIMER_ON_D4 | 41531 | Read Holding register (3) |  | HOLDING REGISTER | INT 16 BIT | 18 | R | PRESET 6 S TON FOR GIVING CLOSE COMAND D4
TIMER_ON_D5 | 41533 | Read Holding register (3) |  | HOLDING REGISTER | INT 16 BIT | 20 | R | PRESET 6 S TON FOR GIVING CLOSE COMAND D5
TIMER_ON_D6 | 41535 | Read Holding register (3) |  | HOLDING REGISTER | INT 16 BIT | 22 | R | PRESET 6 S TON FOR GIVING CLOSE COMAND D6

## Foaie1
Read Register from HORNER RCC 1410
Name | MODBUS ID | MODBUS COMAND SUPPORTED | Bit | Type | Data Type | OFFSET | R/W | Comments
STATUS POWER SOURCE 1 | 10001 | Read Input Status (2) | 0-OPEN 1-CLOSE | DI | BOOL | 0 | R | FEEDBACK POWER SOURCE 1
STATUS POWER SOURCE 2 | 10002 | Read Input Status (2) | 0-OPEN 1-CLOSE | DI | BOOL | 1 | R | FEEDBACK POWER SOURCE 2
STATUS_D1 | 10003 | Read Input Status (2) | 0-OPEN 1-CLOSE | DI | BOOL | 2 | R | CLOSE/OPEN DC SWITCH FEEDBACK D1
STATUS_D2 | 10004 | Read Input Status (2) | 0-OPEN 1-CLOSE | DI | BOOL | 3 | R | CLOSE/OPEN DC SWITCH FEEDBACK D2
STATUS_D3 | 10005 | Read Input Status (2) | 0-OPEN 1-CLOSE | DI | BOOL | 4 | R | CLOSE/OPEN DC SWITCH FEEDBACK D3
STATUS_D4 | 10006 | Read Input Status (2) | 0-OPEN 1-CLOSE | DI | BOOL | 5 | R | CLOSE/OPEN DC SWITCH FEEDBACK D4
STATUS_D5 | 10007 | Read Input Status (2) | 0-OPEN 1-CLOSE | DI | BOOL | 6 | R | CLOSE/OPEN DC SWITCH FEEDBACK D5
STATUS_D6 | 10008 | Read Input Status (2) | 0-OPEN 1-CLOSE | DI | BOOL | 7 | R | CLOSE/OPEN DC SWITCH FEEDBACK D6
STATUS_D7 | 10009 | Read Input Status (2) | 0-OPEN 1-CLOSE | DI | BOOL | 8 | R | CLOSE/OPEN DC SWITCH FEEDBACK D7
STATUS_D8 | 10010 | Read Input Status (2) | 0-OPEN 1-CLOSE | DI | BOOL | 9 | R | CLOSE/OPEN DC SWITCH FEEDBACK D8
Mot_D1 | 17 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 17 | R | CHARGE SPRING D1
Mot_D2 | 20 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 20 | R | CHARGE SPRING D2
Mot_D3 | 23 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 23 | R | CHARGE SPRING D3
Mot_D4 | 26 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 26 | R | CHARGE SPRING D4
Mot_D5 | 29 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 29 | R | CHARGE SPRING D5
Mot_D6 | 1 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 1 | R | CHARGE SPRING D6
Mot_D7 | 4 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 4 | R | CHARGE SPRING D7
Mot_D8 | 7 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 7 | R | CHARGE SPRING D8
MOTOR 1 ON | 18 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 18 | R | CLOSE COMMAND D1
MOTOR 2 ON | 21 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 21 | R | CLOSE COMMAND D2
MOTOR 3 ON | 24 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 24 | R | CLOSE COMMAND D3
MOTOR 4 ON | 27 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 27 | R | CLOSE COMMAND D4
MOTOR 5 ON | 30 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 30 | R | CLOSE COMMAND D5
MOTOR 6 ON | 2 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 2 | R | CLOSE COMMAND D6
MOTOR 7 ON | 5 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 5 | R | CLOSE COMMAND D7
MOTOR 8 ON | 8 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 8 | R | CLOSE COMMAND D8
MOTOR 1 OFF | 19 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 19 | R | OPEN COMMAND D1
MOTOR 2 OFF | 22 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 22 | R | OPEN COMMAND D2
MOTOR 3 OFF | 25 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 25 | R | OPEN COMMAND D3
MOTOR 4 OFF | 28 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 28 | R | OPEN COMMAND D4
MOTOR 5 OFF | 31 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 31 | R | OPEN COMMAND D5
MOTOR 6 OFF | 3 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 3 | R | OPEN COMMAND D6
MOTOR7 OFF | 6 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 6 | R | OPEN COMMAND D7
MOTOR 8 OFF | 9 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 9 | R | OPEN COMMAND D8
MAN_MOT_ON1 | 6001 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 0 | R/W | PUSH BUTON FOR CLOSE DC SWITCH D1
MOTOR 1 ON | 6002 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 1 | R/W | NOT USED
MOTOR 1 OFF | 6003 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 2 | R/W | PUSH BUTON FOR OPENING DC SWITCH D1
MAN_MOT_ON2 | 6004 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 3 | R/W | PUSH BUTON FOR CLOSE DC SWITCH D2
MOTOR 2 ON | 6005 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 4 | R/W | NOT USED
MOTOR 2 OFF | 6006 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 5 | R/W | PUSH BUTON FOR OPENING DC SWITCH D2
MAN_MOT_ON3 | 6008 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 7 | R/W | PUSH BUTON FOR CLOSE DC SWITCH D3
MOTOR 3 ON | 6009 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 8 | R/W | NOT USED
MOTOR 3 OFF | 6010 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 9 | R/W | PUSH BUTON FOR OPENING DC SWITCH D3
MAN_MOT_ON4 | 6012 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 11 | R/W | PUSH BUTON FOR CLOSE DC SWITCH D4
MOTOR 4 ON | 6013 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 12 | R/W | NOT USED
MOTOR 4 OFF | 6014 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 13 | R/W | PUSH BUTON FOR OPENING DC SWITCH D4
MAN_MOT_ON5 | 6016 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 15 | R/W | PUSH BUTON FOR CLOSE DC SWITCH D5
MOTOR 5 ON | 6017 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 16 | R/W | NOT USED
MOTOR 5 OFF | 6018 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 17 | R/W | PUSH BUTON FOR OPENING DC SWITCH D5
MAN_MOT_ON6 | 6020 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 19 | R/W | PUSH BUTON FOR CLOSE DC SWITCH D6
MOTOR 6 ON | 6021 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 20 | R/W | NOT USED
MOTOR 6 OFF | 6022 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 21 | R/W | PUSH BUTON FOR OPENING DC SWITCH D6
MAN_MOT_ON7 | 6024 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 23 | R/W | PUSH BUTON FOR CLOSE DC SWITCH D7
MOTOR 7 ON | 6025 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 24 | R/W | NOT USED
MOTOR 7 OFF | 6026 | Read Input Status (1) | 0-OPEN 1-CLOSE | COIL | BOOL | 25 | R/W | PUSH BUTON FOR OPENING DC SWITCH D7